## Slide 1
Project Title : PU2 - CD4 SCW network monitoring
Location/Unit: SEPL Bukom/ PU2 (CD4) Champion: Ashvini Katkar (Tiger Team) along with PU2 Ops and tech Project Engineer: Rina Yang DPL ID/MTA ID: 211004 / Multiple
Date : 17/10/2022

## Slide 2: High Level Summary for CD4 SCW project:
 | Original Scope | Original Scope – Monitoring (Optimized) | Improved Monitoring Scope | Flushing + Monitoring | Do nothing
Capex, $mln | $2.5 – $3.0 | $2.0 – $2.5 | $0.5 | $0.6 | 0 (or defer to next TA)
Scope | Dead end flushing location (TA) Pumps + RO + stubs, boosted/non booster header (TA & non-TA) Basic monitoring PT/TT/FT (TA) | Dead end flushing location (TA) Pumps + RO + stubs, boosted/non booster header (TA & non-TA) | Basic monitoring PT/TT/FT + 10 x PT (TA) | Dead end flushing FT’s + max. 10 nos. Instruments | As is condition 2 existing booster pumps operating at edge of pump curve.
What it gives us | avoids salting to 3 HX (300k replacement cost each TA) Helps to a large extent to keep HDS3 HP mode operation Better Reliability of SCW network Much better mapping of SCW fouling for next TA | avoids salting to 3 HX (300k replacement cost each TA) Helps to a large extent to keep HDS3 HP mode operation Better Reliability of SCW network No monitoring capability. | Advanced monitoring of the network for better on the run-troubleshooting. | De-debris at E7540AB, E7541ABC, E7439AB. Much better mapping of SCW fouling for next TA | -
Potential consequence, if project is not executed. |  | Difficulty in monitoring & tuning the network. | Accept risk of CD4 potential OA loss (~ 1% annually) Loss of SCW booster pump means HDS3 operates on LP mode (tail gas to flare gas header, multiple thinned sections) Replacement of Ti HX due to salting of 300k per TA. |  | 
Selected option
Phase 1
Notes: 1) Phase2 : Original scope optimized (option 2) to proceed ahead with engineering, so as to achieve FID by Apr 2023 (dependent on Wood availability, after TA 2023 works are concluded)
2) Temp MOC for running 2oo2 booster pump (P7540A/B) has to be converted to permanent. RE has confirmed 2oo2 pump reliable run cannot be assured. Mitigation be discussed as part of permanent MOC. Essential pump/ motor spares to be made available in case any of the pump fail in between (part of permanent MOC). Running both the booster pumps is critical to get sufficient SCW flow to HDS3 HEX’s to enable HP mode of operation. In case of pump failure, HDS3 will go into LP mode of operation.
3) To enable HDS3 LP mode operation, a repair strategy for the 2 flare headers (CD2/4, CD1/5) which needs to take into account redundant CD5 flare header, short term repairs/doability, into question (i.e. we should look beyond clamping thinned sections which require significant alternations to multiple pipe supports). Action is with Utilities Tech team.

## Slide 3: Problem Statement – Phase 1
Insufficient monitoring of CD4 SCW network for pressure and flow
Marine debris accumulation at SCW supply header of elevated HEXs
Proposed solution – Phase 1
To install pressure and flow transmitters at critical location in SCW network
Dead end flushing arrangement to clean up accumulated debris
Notes: E7525-100%
E7524-100%
E7508ABCD- 40%

## Slide 4
Scope summary – Phase 1
TA Scope (Green highlighted in screenshot):
Installation of instrumentation – 6 PTs, 2 FTs
SCW Supply dead end flushing set up

## Slide 5: Scope of E7540A/B, E7539A/B, E7541A/B - SCW Supply Header Dead End flushing arrangement - TA Scope
DEAD END FLUSHING ARRANGEMENT - TA scope
Marine Debris usually collect at the end of header and can plug heat exchanger if agitated.
Header Dead End flushing setup. Similar has been done for ECC CW system.

## Slide 6: Justification
Category |  | 
AI | C (Compliance) | 
 | HSE | 
 | R (Reputation) | 
 | CS (Internal Standards) | 
MM | REL (Reliability) | x
 | IR (Infrastructure Renewal) | 
 | MR (Margin Recovery) | 
GR | G (Growth) | 
VIR | 2.91
 | Justification | 
R A M |  | Rating
 | R+5Y | 
 | Yellow | Asset (D3)
 | Blue | 
Mark with X where applicable
Key in the following score for VIR / MTA / RAM
AIMM – MTA Scoring
AIMM – RAM Rating
GR & MM – VIR
There is dead end header on the supply side of the HEX’s E7540A/B, E7539A/B cluster. These dead end lead to accumulation of debris over a period of time. Once the debris is agitated due to change in flows, et al, pieces of these debris can go into the HEX’s and get stuck at the inlet of the tubes causing tube damages/ leaks in worse case scenario.
VIR is calculated based on estimated 2 weeks shutdown of CD4 due to unavailability of E7540A/B. Likelihood of debris entering causing failures has been taken as once in 20 years.
As per ENS CD4 S/D impact is loss of 27.4 mil /month ~13.5mln for 2 weeks.
Notes: VIR will be more than 1

## Slide 7: Change in cost
CAC @ End Select +/-30% USD $1,670K
------------------------------------------------------------------------------------------
PAC @ End Define +/-10% USD $813K
-----------------------------------------------------------------------------------------
Difference (Decrease) USD $857K
Phasing out of scope to post BBTA 2023 as per alignment meeting with BLT on 21 Sep 22

## Slide 8: Cost Estimate : USD $813K (+/-10%)
------------------------------------------------------------------------------------------
Pre-funding USD $115K 14%
Engineering USD $48K 6%
Procurement USD $142K 17%
Construction USD $352K 43%
Overhead USD $90K 11%
Contingency USD $66K 8%
-----------------------------------------------------------------------------------------
Total Cost USD $813K 100%

## Slide 9: Project LE phasing & Schedule
Execute
Detail Engineering
Define
Full Funding (FID) Approval
Define
(MTS) Scope & Specification
Funding Timeline
  220m of cable trenching to be executed post-TA
Define
Front End
Engineering
Development
Select
Pre-funding
Approval (PDR)
May 22
Mar 22
Mar 24
Capex Allocation | 2022 | 2023 | 2024 | Total
CAPEX (USD) | 50K | 387K | 261K | 698K
Execute Procurement/Award
Sub-Contract
Execute
Construction
Operate
RFSU
Jun to Sep 22
Oct 22
Nov 22 to
Feb 23
Apr 23 to
Mar 24
Oct 22 to
Jun 23

## Slide 11: New additional pressure transmitters (PT) location
E7540AB-22m
E7539 - 22m
E7541A-21m
E7541BC-21m
E7524AB -14m
E7524CD -14m
E7519ABCD – 15m
HEX Failure- CD4100% Crude Impact CD4 Shutdown
HEX Failure- 40% Crude Impact (CD4 Slowdown)
HEX Failure- 20% Crude Impact (CD4 Slowdown)
HEX Failure- 10-15% Crude Impact (CD4 Slowdown)
(S) – Salting Probability HEX
E7516ABCDEF-15m
E7405 (S) -17m
E7407ABC -18m
E7408 -18m
E7406-15m
E7508ABCD (S)-2m
E7536-1m
E7535 (S)-1m
E7512ABC -16m
E7513 -16m
E7511AB (S)-2m
E7515 – 15m
E7522 (S) -3m
E7526 (S) -2m
SCW Supply from PU6
Boosted Header
Non- Boosted Header
2 x 100%
SCW Booster Pumps
E7525 -3m
New additional PT on Non Boosted hdr
New additional PT on Boosted hdr
Existing PT location
75P090
Existing PT location on pump discharge
75PA058/75PG166/167
Clamp-on Ultrasonic flowmeters
PT not required, to be removed
Shift this PT as indicated
Notes: E7525-100%
E7524-100%
E7508ABCD- 40%

## Slide 12: CD4 Heat Exchangers Threats:
Threat Title | MTO Score
I-0206523 (E7536) E7536 High risk of salting on SCW side based on SCW & process side flow/temp | 2,625,000
I-0206465 (E7540A/B,E7539A/B) High vacuum at SCW outlet for E7540AB,E7539,E7541ABC leading erosion in tubes | 125,000
I-0206478 (E7540A/B,E7539A/B) Risk of debris accumulation in the dead end header | 250,000
I-0206476 Lack of SCW flows in E7524 series HEX’s leading to debris accumulation | 2,625,000
I-0206473 Lack of flow instrumentation available to monitor the SCW network in CD4 | 125,000
I-0206472 Lack of temperature instrumentation available to monitor the SCW network in CD4 | 125,000
I-0206466 (E7511A/B) High risk of salting on SCW side based on SCW & process side flow/temp condition | 250,000

## Slide 13: Improved Monitoring of SCW headers- TA Scope
Installation of FT on SCW main headers
Installation of PT on SCW headers

## Slide 14: Complete Scope for CD4 SCW network (Phase 1 + Phase 2)
E7540AB-22m
E7539 - 22m
E7541A-21m
E7541BC-21m
E7524AB -14m
E7524CD -14m
E7536-1m
E7535 (S)-1m
E7522 (S) -3m
SCW Supply from PU6
Boosted Header
Non- Boosted Header
2 x 100%
SCW Booster Pumps
12”
12”
12”
8”
10”
Pumps head increase
Pumps discharge line size increase
Network Monitoring (FT, PT)
New lines to shift 3 HEX tap off from non boosted to boosted header
Line demolition scope
4m long line size reduction to 16”
RO + Valve on SCW outlet lines
E7405 (S) -17m
E7407ABC -18m
E7408 -18m
E7406-15m
Header Dead end flushing
Hydraulic model assessment and Revised scope is based on removal of existing RO at supply of E7519 AB and CD
Also as confirmed with Ops there is no RO on SCW supply for E7524AB on boosted network
Network Monitoring (PT, TT)
Phase 1 scope – CD4 TA 2023 scope
Phase 2 scope – Post TA scope
Notes: E7525-100%
E7524-100%
E7508ABCD- 40%